## Design_Assumption
Category | Parameter | Value | Unit | Basis/Reason
General | Location | Belgium |  | Project assumption
General | Design stage | Concept |  | Early design
General | Operating days | 5 | days/week | Typical industry
General | Operating hours | 8 | h/day | Day shift
General | Outside design temp (summer) | 30 | °C | Typical BE
General | Outside Design Temp (winter) | -5 | °C | Typical BE
Indoor | Office temp | 22 | °C | Comfort
Indoor | Office RH | 50 | % | Comfort
Indoor | Industrial hall temp | 18-26 | °C | Process tolerance
Indoor | Cleanroom temp | 21 | °C | Process-driven
Indoor | Cleanroom RH | 50 | % | Process-driven
Ventilation | Office fresh air per person | 36 | m³/h.person | EN typical
Ventilation | Office occupancy density | 2026-01-10 | person/m² | Assume
Ventilation | Industrial hall ACH | 2 | 1/h | Conservative
Ventilation | Cleanroom ACH | 20 | 1/h | Conservative
HVAC | Cooling System | Chilled water |  | Central Plant
HVAC | Heating System | Heat Pump |  | EU trend
HVAC | Office AHU type | Recirculatoin |  | Energy efficiency
HVAC | Cleanroom AHU type | One-through |  | Contamination control
HVAC | Heat recovery | Yes |  | EPB awareness
Units | Power unit | kW |  | EU standard
Units | Airflow unit | m³/h |  | BE practice
Units | Pump flow unit | m³/h |  | Consistency
Units | Pressure unit | Pa/bar |  | HVAC convection